TCU HEAT LOAD SIMULATOR

Project Context Summary

For use in new conversation — complete project background

| Project | TCU Heat Load Simulator |
| --- | --- |
| Engineer | Howard (CE Student Intern) |
| Organisation | SSMC — Semiconductor Manufacturing |
| Budget target | USD 4,800 (98% saving vs vendor quote of USD 19,800) |
| Timeline | 6 Mar 2026 – 6 Apr 2026 |
| Current phase | Phase 1 — App + web dashboard feature complete, RPi + touchscreen pending delivery |
| Phase 2 | Smart heater + AI platform (future) |

# 1. Project Background

## 1.1 Problem Statement

SSMC operates ASML photo tools (scanners) in the fab. Each tool is cooled by a Haake ASM TCU that maintains the tool at 22°C. When a TCU is sent for repair, post-repair testing does NOT simulate the actual heat load from the photo tool. A repaired TCU may pass the current test but fail in production.

External vendor quoted USD 19,800 for a test jig. Project goal: build a TCU heat load simulator under USD 4,800.

## 1.2 Decision: Improve Existing In-House Jig

An existing heat loader (SAP: 401087) was found in the workshop. Decision: improve it rather than build new, saving ~SGD 800+ in electrical panel hardware. Key improvements:

- Add Raspberry Pi 4 + 15.6" touchscreen for monitoring and logging

- Connect to Haake TCU via RS232 (FTDI USB adapter, confirmed working)

- Add PZEM-004T energy meter via GPIO UART for true watts measurement

- Add RCCB for CP5 electrical safety compliance

- Run PyQt5 GUI app for live monitoring, pass/fail logic, CSV logging

# 2. Hardware Configuration

## 2.1 Haake ASM TCU

| Parameter | Value |
| --- | --- |
| RS232 interface | 25-pin Sub-D, 2400 baud, 8N1, straight-through DB9 F-F cable |
| Temperature range | 17°C to 27°C, setpoint 22.0°C |
| Cooling capacity | 1200W at 20°C outlet (design basis) |
| Flow rate | 50 ℓ/min at 0.5 bar ΔP |
| Internal sensor | PT500 (read via RS232 M command, not wired directly) |
| Normal BS status | 400000 hex (b1=0x40 = waterbath FULL, expected) |

## 2.2 RS232 Command Reference

| Command | Response | Description |
| --- | --- | --- |
| M<CR> | XX.XX C$ | Inlet fluid temperature (°C) |
| D<CR> | XX.X l/min$ | Flow rate — parsed as float not int |
| SOLL<CR> | XX.XX$ | Read current setpoint |
| BS<CR> | XXXXXX$ | Status bytes — 3 bytes hex |
| START<CR> | $ | Start temperature control |
| STOP<CR> | $ | Stop temperature control |
| AFV<CR> | status stream | Fill system and pre-temperature control |
| ER<CR> | $ | Release alarm after fault cleared |

## 2.3 Serial Connection — Confirmed Working

| Item | Detail |
| --- | --- |
| Adapter | FTDI DT5011 USB-RS232, DB9 Female |
| Cable | Straight-through DB9 F-F (NOT crossover) |
| Windows port | COM5 (Toshiba Portege) |
| Linux port | /dev/ttyUSB0 (Raspberry Pi) |
| Settings | 2400 baud, 8N1, no handshake, rtscts=False, dsrdtr=False |
| Test response | 21.93 C$ (inlet temp), 00.0 l/min$ (flow), 400000 (status) |

## 2.4 Existing Jig Hardware

| Component | Model | Status |
| --- | --- | --- |
| PLC | Panasonic FP0-C14CRS | Undocumented — FPWIN Pro 7.5 + AFC8503 cable needed |
| HMI | Panasonic GT02 | Operator selects 500W/1000W/2000W stages |
| Heater | Reach Electrical 262627, 2kW | 2000W stage delivers ~1403W actual (confirmed) |
| Power regulator | HoTTemP W5 SCR | Phase angle control — analogue scaling wrong at low stages |
| Contactor | Schneider TeSys | Controlled by FP0 PLC |
| PSU | Mean Well LRS-100-24 | Powers PLC and HMI |

## 2.5 PZEM-004T Energy Meter

| Item | Detail |
| --- | --- |
| Model | Peacefair PZEM-004T v3.0 with 100A open split-core CT |
| Connection | RPi GPIO UART — TX pin 8 (GPIO14), RX pin 10 (GPIO15), 5V pin 2, GND pin 6 |
| Linux port | /dev/ttyAMA0 (requires dtoverlay=disable-bt in config.txt) |
| Windows port | COM6 (USB-TTL adapter if testing on Toshiba) |
| Protocol | Modbus RTU, 9600 baud, slave 0xF8, integer-scaled registers (not IEEE 754) |
| CT installation | Open CT clips around heater live wire — no rewiring needed |
| L/N wiring | Tap from W5 output terminals — measures actual watts delivered to heater |
| Key registers | Voltage: 0x0000 (÷10), Current: 0x0001-2 (÷1000), Power: 0x0003-4 (÷10) |

# 3. Software Architecture

## 3.1 Platform

PyQt5 GUI application. Runs on Windows (Toshiba, COM5) and Linux/RPi (/dev/ttyUSB0) — platform auto-detected via sys.platform at startup. No manual config changes needed when switching.

Run: python3 main.py (Linux) or python main.py (Windows PowerShell — NOT WSL)

Install: pip install -r requirements.txt (PyQt5, pyqtgraph, pyserial, minimalmodbus)

## 3.2 File Structure

| File | Responsibility | Key Notes |
| --- | --- | --- |
| config.py | All settings — reads from settings_manager at import | Auto-detects Windows/Linux for port names |
| settings_manager.py | Loads/saves settings.json — singleton | Callback system for hot reload |
| translations.py | EN/ZH/MS string dict — tr(key) function | Used by all GUI tabs |
| ipc.py | IPC abstraction layer | JSON file on Windows, Unix socket on Linux/RPi |
| web_server.py | Flask web server — separate process | Serves phone dashboard at tcuplusplus.local:5000 |
| generate_vapid.py | VAPID key generator — run once | Required for push notifications |
| tcu_comms.py | RS232 to Haake TCU | flow rate parsed as float (not int) |
| pzem004t.py | PZEM-004T Modbus RTU energy meter | GPIO UART on RPi, integer-scaled registers |
| daq_thread.py | Configurable rate DAQ thread | Writes to IPC on every sample for web server |
| logger_thread.py | CSV logger thread | Decoupled from DAQ — never blocks sampling |
| test_logic.py | Pass/fail + alarm parsing + BS decode | decode_status(), is_abnormal() — correct b2 bit 2 |
| gui/main_window.py | Top-level window — TCU++ | Hot reload: theme, language, settings, ports |
| gui/monitor_tab.py | Live TCU readings + graph | retranslate(), refresh_settings() implemented |
| gui/test_tab.py | Heat load test tab | retranslate(), refresh_settings() implemented |
| gui/settings_tab.py | Settings UI — ports, params, theme, language | Persists to settings.json — hot reload on apply |
| gui/docs_tab.py | Built-in documentation | 6 sub-tabs: TCU specs, RS232, BS bytes, procedure, PZEM, alarms |
| gui/styles.py | Light/dark theme — dynamic scaling | get_app_style(scale, theme) — scale from screen width |
| start.sh | Linux launcher | Checks /dev/ttyUSB0 and /dev/ttyAMA0 |

## 3.3 Key Config Values

| Setting | Current Value | Notes |
| --- | --- | --- |
| TEST_DURATION_MIN | 180 | Changed from 30 min |
| TEMP_SETPOINT | 22.0 | °C |
| TEMP_TOLERANCE | 0.5 | °C — changed from 0.1 (was failing threshold) |
| MIN_FLOW_RATE | 1 | ℓ/min |
| TCU_PORT | Auto: COM5 (Win) / /dev/ttyUSB0 (Linux) |  |
| PZEM_PORT | Auto: COM6 (Win) / /dev/ttyAMA0 (Linux) |  |
| PZEM_SLAVE | 0xF8 | PZEM-004T broadcast address |
| PZEM_BAUD | 9600 | PZEM-004T default |
| LOG_DIR | logs/ | CSV output folder — excluded from git |

## 3.4 DAQ Sample Dataclass Fields

| Field | Source | Type |
| --- | --- | --- |
| inlet_temp | TCU RS232 M command | float ¦ None |
| flow_rate | TCU RS232 D command (float) | float ¦ None |
| setpoint | TCU RS232 SOLL command | float ¦ None |
| b1, b2, b3 | TCU RS232 BS command | int ¦ None |
| alarms | Parsed from b1/b2/b3 | List[str] |
| voltage | PZEM-004T register 0x0000 | float ¦ None |
| current | PZEM-004T registers 0x0001-2 | float ¦ None |
| power | PZEM-004T registers 0x0003-4 (true watts) | float ¦ None |
| raw_log | RS232 command/response string | str |

## 3.5 CSV Log Columns

| Column | Source |
| --- | --- |
| Timestamp | HH:MM:SS |
| Elapsed (min) | Time since test start |
| Setpoint (C) | TCU SOLL command |
| Inlet Temp TCU (C) | TCU M command |
| Flow (L/min) | TCU D command |
| Voltage (V) | PZEM-004T |
| Current (A) | PZEM-004T |
| Power (W) | PZEM-004T — true watts, handles phase angle SCR |
| Alarms | Parsed BS status bytes |
| Mode | MONITOR or TEST |
| Status | RUNNING / PASS / FAIL with reason |

# 4. Pass/Fail Criteria

| Criteria | Threshold | Source |
| --- | --- | --- |
| Inlet temperature | 22.0°C ±0.5°C for full 180 min (manager’s requirement) | TCU RS232 M command |
| Flow rate | ≥1 ℓ/min continuously | TCU RS232 D command |
| TCU alarms | No alarms (BS = 400000) | TCU RS232 BS command |
| Test duration | 180 minutes (manager’s requirement) | Software timer |

# 5. Bill of Materials (Confirmed Prices — April 2026)

| # | Component | SGD | Notes |
| --- | --- | --- | --- |
| 1 | Raspberry Pi 4 Model B 4GB (RPI4-MODBP-4GB) | 102.40 | Procured March 2026 |
| 2 | AUGUSTINA Durable Case ABS + Cooling Fan | 6.27 | GPIO pins 2/4 (5V) + 6/9 (GND) for fan + PZEM |
| 3 | Official RPi USB-C PSU 5.1V 3A (MP001636) | 18.58 | Powers RPi 4 — 3A required minimum |
| 4 | 15.6" HDMI LCD Touchscreen with Case | 235.00 | HDMI + USB touch — confirmed SGD 235 |
| 5 | USB-to-RS232 Adapter FTDI DT5011 DB9F | 25.00 | Confirmed working COM5 / /dev/ttyUSB0 |
| 6 | Panasonic AFC8503 PLC Programming Cable | 81.10 | Panasonic SG quotation — for FPWIN Pro 7.5 |
| 7 | Peacefair PZEM-004T v3.0 100A + open CT | 45.00 | GPIO UART — no USB port used |
| 8 | RCCB 2P 40A 30mA AC type (HORME Singapore) | 55.90 | CP5 compliance — earth leakage protection |
|  | TOTAL | 569.25 | Existing jig hardware SGD 0 (in-house assets) |

Full BOM with specifications and suppliers: TCU_BOM_Final.xlsx

Phase 2 BOM (Smart Heater + AI Platform): TCU_BOM_plusplus_v2.xlsx

# 6. Key Decisions

| Topic | Decision |
| --- | --- |
| Platform | Raspberry Pi 4 4GB — not Toshiba CF-19 (liability concerns) |
| Display | 15.6" HDMI touchscreen — not RPi 7" DSI (better screen size for workshop) |
| Energy meter | PZEM-004T via GPIO UART — not SDM120-MOD (unavailable locally, saves USB port) |
| CT type | Open/split-core — clips around wire, no rewiring needed |
| Heat load stage | 2000W stage (~1403W actual) — exceeds 1200W rated load |
| PT100 sensor nodes | Removed — ΔT at 50 L/min is 0.4°C, smaller than ±0.42°C sensor uncertainty |
| Temperature tolerance | 0.5°C — changed from 0.1°C on manager’s request |
| Test duration | 180 minutes — changed from 30 minutes on manager’s request |
| Settings persistence | settings_manager.py saves to settings.json — survives restart |
| Hot reload | Theme, language, ports, test params all hot reload without restart |
| Language support | English, Chinese (Simplified), Malay — tr(key) in all GUI tabs |
| UI scaling | scale = screen.width()/1920 clamped 0.65–1.0 — auto-fits 13″ and 15.6″ |
| Light mode | Default theme is light — dark mode available in Settings tab |
| Documentation tab | 6 sub-tabs: TCU specs, RS232, BS bytes, test procedure, PZEM wiring, alarm guide |
| BS status decoding | b2 bit 2 = main contactor ON (normal) — 400400 is healthy running state |
| Poll interval | Default 1s — configurable in Settings tab — updates DAQ thread live |
| Phone web app | Flask web server + plain HTML/JS PWA — no framework, no app store install |
| Web app access | http://tcuplusplus.local:5000 — mDNS via Avahi on RPi |
| Web app auth | Username/password in users.json (SHA-256 hashed) — managed by admin |
| Web app roles | Technician (full control) / Supervisor (view only) |
| Operator lock | One technician at a time — FIFO queue by login time — 5 min inactivity timeout |
| Touchscreen priority | Physical RPi touchscreen always overrides web operators |
| Push notifications | Web Push + VAPID keys + service worker — works when browser closed |
| IPC layer | JSON file on Windows, Unix socket on Linux — auto-selected via sys.platform |
| Web server process | Separate process from PyQt5 app — started manually, runs independently |
| PXE boot | Hard requirement (fab policy — no SD cards) — IT request drafted |
| RCCB | ABB 2P 40A 30mA — SGD 55.90, mandatory for CP5 compliance |
| NAS/storage | IT to provision shared network drive — no NAS purchased |
| Code structure | PyQt5 + threading — DAQ thread / Logger thread / GUI thread decoupled |
| Platform portability | sys.platform auto-detects Windows vs Linux — ports set automatically |
| Windows sleep | SetThreadExecutionState called on test start, released on test end |
| Git workflow | main branch — single codebase for both Windows and RPi |

# 7. Pending Items

## 7.1 Hardware (blocked on external dependencies)

| Item | Status |
| --- | --- |
| AFC8503 cable | Quoted SGD 81.10 — procurement in progress |
| RPi 15.6" touchscreen | On order — SGD 235 confirmed |
| PZEM-004T + CT | On order — SGD 45 confirmed |
| ABB RCCB | On order — SGD 55.90 confirmed |
| RPi GPIO UART setup | Run raspi-config + dtoverlay=disable-bt before connecting PZEM |
| Electrician — wiring diagram | Required for CP5 compliance before jig use |
| Electrician — PZEM wiring | Tap L/N from W5 output, clip CT around heater live wire |
| Electrician — RCCB installation | Install in existing panel |
| FP0 PLC ladder logic | Read with FPWIN Pro 7.5 + AFC8503 — fix analogue scaling at 500W/1000W |
| Full 180-min validation test | Run with TCU on RPi once touchscreen arrives |

## 7.2 IT / Infrastructure (blocked on IT)

| Item | Status |
| --- | --- |
| PXE boot server | IT request drafted — requesting Linux laptop + dnsmasq + nfs-kernel-server + RPi network registration |
| SD card policy exception | Alternative to PXE boot — pursuing as simpler short-term solution |
| IT shared drive | Network drive address for CSV auto-upload after each test |

## 7.3 Hardware (blocked on external dependencies)

| Item | Status |
| --- | --- |
| AFC8503 cable | Quoted SGD 81.10 — procurement in progress |
| RPi 15.6” touchscreen | On order — SGD 235 confirmed |
| PZEM-004T + CT | On order — SGD 45 confirmed |
| ABB RCCB | On order — SGD 55.90 confirmed |
| RPi GPIO UART setup | Run raspi-config + dtoverlay=disable-bt before connecting PZEM |
| Electrician — wiring diagram | Required for CP5 compliance before jig use |
| Electrician — PZEM wiring | Tap L/N from W5 output, clip CT around heater live wire |
| Electrician — RCCB installation | Install in existing panel |
| FP0 PLC ladder logic | Read with FPWIN Pro 7.5 + AFC8503 — fix analogue scaling at 500W/1000W |
| Full 180-min validation test | Run with TCU on RPi once touchscreen arrives |

## 7.4 Web Dashboard (pending workshop verification)

| Item | Status |
| --- | --- |
| Live readings from DAQ | Pending — needs TCU connected in workshop |
| TCU commands from phone | Pending — needs TCU connected in workshop |
| Test start/stop from phone | Pending — needs TCU connected in workshop |
| Push notifications | Pending — needs VAPID keys generated + phone grant permission |
| tcuplusplus.local hostname | Pending — needs Avahi on RPi (sudo apt install avahi-daemon) |
| Multiple operators on workshop WiFi | Pending — needs RPi on workshop network |

# 8. Phase 2 — Smart Heater + AI Platform + Phone Web App (Future)

Phase 2 is planned but not yet started. See TCU_BOM_plusplus_v2.xlsx for full BOM (SGD 886 / USD 656).

| Component | Role | Notes |
| --- | --- | --- |
| CrowPanel 7.0" ESP32 | Smart heater controller (NOT master CPU) | Inside heater unit — controls SSR, reads INA226 + PT100 |
| SSR 40A (Fotek) | Replaces HoTTemP W5 | PWM from ESP32 — dynamic wattage control |
| INA226 | Watts measurement inside heater | Replaces PZEM in Phase 2 |
| MAX31865 + PT100 | Outlet water temp | Inside smart heater unit |
| Thermocouple + MAX6675 | Element health monitoring | Rising baseline = degradation |
| TensorFlow / scikit-learn | AI on RPi 4 | Anomaly detection, predictive maintenance, profile learning |
| WebSocket server | RPi bridges TCU data to phone | Flask/FastAPI — served on workshop WiFi |
| Phone web app | Operator monitoring from phone | PWA — works on Android + iOS, no install needed |
| IT shared drive | Log storage (no NAS) | RPi uploads CSV via WiFi after each test |

# 9. Project Folder Structure

Repository: ~/projects/tcu-heat-loader/

| Folder / File | Purpose |
| --- | --- |
| tcu_app/ | Main PyQt5 application — runs on RPi 4 |
| tcu_app/gui/ | GUI modules (main_window, monitor_tab, test_tab, settings_tab, docs_tab, styles) |
| tcu_app/ipc.py | IPC abstraction — JSON on Windows, Unix socket on Linux |
| tcu_app/web_server.py | Flask web server — separate process, serves phone dashboard |
| tcu_app/generate_vapid.py | Run once to generate VAPID keys for push notifications |
| tcu_app/users.json | User credentials — gitignored, managed by admin |
| tcu_app/vapid_keys.json | Push notification keys — gitignored, generated by generate_vapid.py |
| tcu_app/logs/ | CSV test logs — gitignored, runtime output |
| tcu_app/settings.json | User settings — gitignored, machine-specific |
| web/ | Phone web app — HTML/JS/CSS served by Flask |
| web/index.html | Login page |
| web/dashboard.html | Main dashboard (monitor + test tabs) |
| web/app.js | Frontend logic — polling, lock management, charts, toasts |
| web/style.css | Light mode styling — mobile first |
| web/manifest.json | PWA manifest — enables Add to Home Screen |
| web/sw.js | Service worker — handles push notifications when browser closed |
| heater_app/ | Phase 2: MicroPython for CrowPanel ESP32 smart heater |
| docs/ | BOM files, manuals, project context document |
| README_web.md | Web server setup and usage documentation |
| .gitignore | At repo root — ignores logs/, settings.json, users.json, vapid_keys.json, .tcu_ipc.json, .tcu_cmd.json |

# 10. How to Continue in New Conversation

Paste the following prompt and attach this document and TCU_BOM_Final.xlsx:

I am continuing a TCU Heat Load Simulator project for SSMC. Please read TCU_Project_Context.docx for full background. The project uses a Haake ASM TCU, Raspberry Pi 4, PyQt5 GUI app (TCU++), PZEM-004T energy meter via GPIO UART, and existing in-house heat loader jig. Phase 1 app + phone web dashboard are feature complete — running on Toshiba (testing), RPi and touchscreen on order. Web dashboard tested and working (login, lock system, supervisor role verified). Pending: RPi workshop setup, TCU command verification with hardware, push notifications, PXE boot (IT request drafted), full 180-min validation test.

— End of Project Context Summary — TCU Heat Load Simulator — SSMC Internal